## 9M actions
Recommendation ID | M | Change | HoC tier | Corrective/Preventive | Indicator | Owner | Due date | Status | Notes
m1-3 | M1 | Corrective: remove the field reseal task from this class of joint, so that no crew has to judge the part, the method and the test alone. Pressure-boundary seals on the metering skid are restored by exchanging a shop-built assembly that has already passed its pressure test. | elimination | Corrective | Pressure-boundary seal jobs on the skid done by assembly exchange, as a share of all such jobs
m2-3 | M2 | Preventive: remove the need for anyone to approach a release to isolate it. Every emergency isolation point for the metering area is worked from outside the area a release can cover. | elimination | Preventive | Emergency isolation points on the skid that can be worked without entering the release zone
m3-3 | M3 | Preventive: remove the seal that could be swapped without a risk assessment. Replace the O-ring-sealed joints on the metering pressure boundary with welded connections where the design allows, so no seal is left to substitute outside the management-of-change process. | elimination | Preventive | Seal-dependent joints left on the metering pressure boundary (count)
m4-3 | M4 | Corrective: remove the ignition sources the doctrine left to run to breakdown. Move electrical equipment that does not need to be in the Zone 1 metering area out of it, so a major leak there finds nothing to ignite while isolation is decided. | elimination | Corrective | Electrical items inside the Zone 1 metering area that do not need to be there (count)
m5-3 | M5 | Corrective: remove a known-defective item from the gas path. A pressure-boundary item with an open malfunction notification, such as the failed meter, is spaded out of the gas path until it is repaired and the notification is closed, so no gas flows through an item whose warning is still waiting for a response. | elimination | Corrective | Pressure-boundary items left in the gas path with an open malfunction notification (count)
m6-3 | M6 | Corrective: fund the removal of the hazard the unassessed emergency-valve programme left in place. Budget the replacement of the hand-worked emergency valves, so that isolating the terminal no longer depends on anyone entering the release area. | elimination | Corrective | Hand-worked emergency isolation valves left in the terminal's release zones (count)
m7-3 | M7 | Corrective: retire the 1986 meter and its rectangular-slot joint, removing the seal that failed four times, and replace it with a design whose seal is specified and stocked. | elimination | Corrective | Metering-skid joints in service with two or more seal failures in 24 months (count)
m8-3 | M8 | Preventive: remove unspecified seals from supply. Stores and purchasing hold and buy no pressure-boundary seal without an approved specification, so there is no unspecified part to fit. | elimination | Preventive | Pressure-boundary seals in stores without an approved specification (count)
m9-3 | M9 | Preventive: remove the repeat-reseal path. An item whose seal fails a second time leaves routine maintenance and stays out of service until its root cause is found and fixed. | elimination | Preventive | Items with a second seal failure returned to service before a root-cause review (count)