## Slide 1
Safety Moment: Test what you disturb (Gas terminal release and fire, 2020)
Audience: Session leaders (T2): maintenance and shift supervisors and trainers running a ten-minute session for maintenance and instrument crews (T1)
Incident: Hazira gas terminal condensate release and fire · 2020-09-24
Learning purposes: not a statutory document. Derived from a ProbeMatrix investigation export; learnings are evidence-linked but should be validated by the organisation before adoption. Draft learnings: the investigation status is in progress. · Learnings drafted by an AI agent from AI-assisted findings
DRAFT
Review: draft · Classification: internal · Version 1.0
Draft because: the investigation status is in progress; no finding is marked as edited by a person
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Audience: Session leaders (T2): maintenance and shift supervisors and trainers running a ten-minute session for maintenance and instrument crews (T1)
Incident: Hazira gas terminal condensate release and fire · 2020-09-24
Learning purposes: not a statutory document. Derived from a ProbeMatrix investigation export; learnings are evidence-linked but should be validated by the organisation before adoption. Draft learnings: the investigation status is in progress. · Learnings drafted by an AI agent from AI-assisted findings
DRAFT
Review: draft · Classification: internal · Version 1.0
Draft because: the investigation status is in progress; no finding is marked as edited by a person
Data quality and limits:
- Draft learnings from an unreviewed analysis: the export's investigation status is in progress and no finding is marked as edited by a person. Validate every item before the session.

## Slide 2
Bottom line
No specification, no fit: a seal that does not match the original is a change, not a spare.
A joint you opened is not proven until it has passed a recorded test to the written test pressure.
When the same fault comes back, say so on the job record; a repeat is a warning, not a routine job.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: No specification, no fit: a seal that does not match the original is a change, not a spare.
Cites: FND-8C0BB623; EVD-8645
A joint you opened is not proven until it has passed a recorded test to the written test pressure.
Cites: FND-212DC9B7; EVD-2894
When the same fault comes back, say so on the job record; a repeat is a warning, not a routine job.
Cites: FND-69067A1C; EVD-1494
Cited records:
FND-8C0BB623: Maintenance Team - Gasket Replacement Without OEM Spec · L1 · rating 4
EVD-8645: document
FND-212DC9B7: Maintenance Team - No Hydrostatic Test After Gasket Replacement · L1 · rating 4
EVD-2894: document
FND-69067A1C: Chronically failing meter 310FT01 kept in service across three gasket replacements in 22 months · L2 · rating 4
EVD-1494: document

## Slide 3
What happened
On 18 Sep 2020 the seal on a 1986 condensate meter at the gas terminal was changed. The maker's specification had been lost, so a locally bought round O-ring was fitted, as had become regular practice, and the system was brought only to operating pressure, with no test to design pressure. The meter went back on line the next day and was in use on 24 Sep, when that seal was the probable source of a release that later caught fire.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. On 18 Sep 2020 the seal on a 1986 condensate meter at the gas terminal was changed. The maker's specification had been lost, so a locally bought round O-ring was fitted, as had…
Text: On 18 Sep 2020 the seal on a 1986 condensate meter at the gas terminal was changed. The maker's specification had been lost, so a locally bought round O-ring was fitted, as had become regular practice, and the system was brought only to operating pressure, with no test to design pressure [FND-8C0BB623; FND-212DC9B7; EVD-8645; EVD-2894]. The meter went back on line the next day and was in use on 24 Sep, when that seal was the probable source of a release that later caught fire [FND-15279F97; EVD-2894].
Cites: FND-8C0BB623; FND-212DC9B7; EVD-8645; EVD-2894; FND-15279F97
Cited records:
FND-8C0BB623: Maintenance Team - Gasket Replacement Without OEM Spec · L1 · rating 4
FND-212DC9B7: Maintenance Team - No Hydrostatic Test After Gasket Replacement · L1 · rating 4
EVD-8645: document
EVD-2894: document
FND-15279F97: Post-maintenance testing - 18 Sep 2020 gasket replacement · L1 · rating 4

## Slide 4
Did you know?
The meter was built for a rectangular-slot gasket; the round O-ring was a local substitute, bought with no specification or quality check.
This was the third seal change on the same meter in about 22 months, and a malfunction notification had been raised the day before the last one. None of the repeats led to a review of why it kept leaking.
No written procedure covered testing these high-pressure meters before they went back into service, so holding at operating pressure became the normal check.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. The meter was built for a rectangular-slot gasket; the round O-ring was a local substitute, bought with no specification or quality check.
Text: The meter was built for a rectangular-slot gasket; the round O-ring was a local substitute, bought with no specification or quality check [FND-7A32AC87; EVD-8645].
Cites: FND-7A32AC87; EVD-8645
2. This was the third seal change on the same meter in about 22 months, and a malfunction notification had been raised the day before the last one. None of the repeats led to a…
Text: This was the third seal change on the same meter in about 22 months, and a malfunction notification had been raised the day before the last one. None of the repeats led to a review of why it kept leaking [FND-69067A1C; FND-82FC718D; EVD-1494; EVD-0591].
Cites: FND-69067A1C; FND-82FC718D; EVD-1494; EVD-0591
3. No written procedure covered testing these high-pressure meters before they went back into service, so holding at operating pressure became the normal check.
Text: No written procedure covered testing these high-pressure meters before they went back into service, so holding at operating pressure became the normal check [FND-257C1100; EVD-2894].
Cites: FND-257C1100; EVD-2894
Cited records:
FND-7A32AC87: Maintenance Team - Wrong Choice: Substitute O-ring for OEM Rectangular-Slot Gasket · L1 · rating 4
EVD-8645: document
FND-69067A1C: Chronically failing meter 310FT01 kept in service across three gasket replacements in 22 months · L2 · rating 4
FND-82FC718D: Recurring gasket failures on 310FT01 treated as routine maintenance instead of reliability warning · L4 · rating 4
EVD-1494: document
EVD-0591: log_record
FND-257C1100: No standard operating procedure existed for calibration and return-to-service of the high-pressure meters, including mandatory hydrotest to design pressure · L3 · rating 4
EVD-2894: document

## Slide 5
What you can do
Check the part against the groove and the specification before you fit it. If nobody can show a specification, stop and ask the supervisor.
Before you hand the equipment back, ask for the written test pressure and the witness, and write the test result on the job record; if no test was done, write that.
Write "repeat failure" on the job record when you fix the same fault again, and tell the supervisor how often you have seen it.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Check the part against the groove and the specification before you fit it. If nobody can show a specification, stop and ask the supervisor.
Text: Check the part against the groove and the specification before you fit it. If nobody can show a specification, stop and ask the supervisor.
When: before fitting a seal or gasket on a pressure part
Cites: FND-89962239; EVD-8645
2. Before you hand the equipment back, ask for the written test pressure and the witness, and write the test result on the job record; if no test was done, write that.
Hold point: yes
Text: Before you hand the equipment back, ask for the written test pressure and the witness, and write the test result on the job record; if no test was done, write that.
When: before return to service
Cites: FND-15279F97; EVD-2894
3. Write "repeat failure" on the job record when you fix the same fault again, and tell the supervisor how often you have seen it.
Text: Write "repeat failure" on the job record when you fix the same fault again, and tell the supervisor how often you have seen it.
When: when a fault comes back
Cites: FND-69067A1C; EVD-1494
Cited records:
FND-89962239: Gasket replacement using non-standard material - 18 Sep 2020 · L1 · rating 4
EVD-8645: document
FND-15279F97: Post-maintenance testing - 18 Sep 2020 gasket replacement · L1 · rating 4
EVD-2894: document
FND-69067A1C: Chronically failing meter 310FT01 kept in service across three gasket replacements in 22 months · L2 · rating 4
EVD-1494: document

## Slide 6
Questions for the crew
Which pressure parts on our unit have no specification we can find?
What test proves a joint we have just made, and where is the result written?
Which items do we keep fixing, and who decides whether we repair again or look for the cause?
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Which pressure parts on our unit have no specification we can find?
Question: Which pressure parts on our unit have no specification we can find?
Why it matters: The seal on this meter had no specification on file, so a substitute became the normal part [FND-B356F15B; EVD-8645].
Answer: A good answer names the parts, where their specification should be kept, and who the crew asks when a spare differs from the original.
Cites: FND-B356F15B; EVD-8645
2. What test proves a joint we have just made, and where is the result written?
Question: What test proves a joint we have just made, and where is the result written?
Why it matters: After the seal change the system was only brought to operating pressure, with no test to design pressure [FND-7C5ED5B3; EVD-2894].
Answer: A good answer gives the test, the test pressure, who witnesses it and where the result is recorded before operations accept the equipment.
Cites: FND-7C5ED5B3; EVD-2894
3. Which items do we keep fixing, and who decides whether we repair again or look for the cause?
Question: Which items do we keep fixing, and who decides whether we repair again or look for the cause?
Why it matters: Repeat seal failures on this meter were handled as routine repairs [FND-82FC718D; EVD-1494].
Answer: A good answer names the items, says where a repeat would show on the job record, and names the role that starts a cause review.
Cites: FND-82FC718D; EVD-1494
Cited records:
FND-B356F15B: Gasket Replacement Procedure - Material Specification Bypass · L1 · rating 4
EVD-8645: document
FND-7C5ED5B3: Maintenance Team - Hydrostatic Test Requirement After Gasket Replacement · L1 · rating 4
EVD-2894: document
FND-82FC718D: Recurring gasket failures on 310FT01 treated as routine maintenance instead of reliability warning · L4 · rating 4
EVD-1494: document

## Slide 7
Narration
Test what you disturb
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Test what you disturb
Title: Test what you disturb
Channel: video
Purpose: A one-minute clip to open the session before the questions.
Segments:
- {"visual": "A metering skid, and an old meter with its retaining plate off.", "narration": "This condensate meter dated from 1986. Its seal had been changed three times in under two years.", "seconds": 15, "on_screen": "Same meter, third seal change", "cites": ["FND-69067A1C", "EVD-1494"]}
- {"visual": "A round O-ring held next to a rectangular groove.", "narration": "The maker's specification was lost, so a locally bought O-ring was fitted, as usual.", "seconds": 15, "on_screen": "No specification, no fit", "cites": ["FND-8C0BB623", "EVD-8645"]}
- {"visual": "A pressure gauge rising to its normal operating mark and stopping there.", "narration": "The joint was held at operating pressure and handed back. It was never tested to design pressure.", "seconds": 15, "on_screen": "Test to the written pressure", "cites": ["FND-212DC9B7", "EVD-2894"]}
- {"visual": "A crew member writes a test result on a job record and shows it to the supervisor.", "narration": "Six days later that seal was the probable source of a release that caught fire. Before you hand back, ask for the test.", "seconds": 15, "on_screen": "No recorded test, no hand-back", "cites": ["FND-15279F97", "EVD-2894"]}
Cites: FND-8C0BB623; FND-212DC9B7; FND-69067A1C; EVD-1494; EVD-8645; EVD-2894; FND-15279F97
Cited records:
FND-8C0BB623: Maintenance Team - Gasket Replacement Without OEM Spec · L1 · rating 4
FND-212DC9B7: Maintenance Team - No Hydrostatic Test After Gasket Replacement · L1 · rating 4
FND-69067A1C: Chronically failing meter 310FT01 kept in service across three gasket replacements in 22 months · L2 · rating 4
EVD-1494: document
EVD-8645: document
EVD-2894: document
FND-15279F97: Post-maintenance testing - 18 Sep 2020 gasket replacement · L1 · rating 4

## Slide 8
Coverage
This pack cites 8 of 128 relevant findings.
8 of 49 top-rated relevant findings cited.
Learning purposes: not a statutory document. Derived from a ProbeMatrix investigation export; learnings are evidence-linked but should be validated by the organisation before adoption. Draft learnings: the investigation status is in progress. · Learnings drafted by an AI agent from AI-assisted findings
Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: This pack cites 8 of 128 relevant findings.
8 of 49 top-rated relevant findings cited.
Learning purposes: not a statutory document. Derived from a ProbeMatrix investigation export; learnings are evidence-linked but should be validated by the organisation before adoption. Draft learnings: the investigation status is in progress. · Learnings drafted by an AI agent from AI-assisted findings
Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
Limits of this pack:
- This session is built from the frontline Learning Cards for LR-01, LR-02 and LR-05 and uses the same story; the cards are what the crew keep afterwards.
- The organisation's fixes (re-establishing the specification, a return-to-service procedure, a repeat-failure trigger) are for supervisor-coach and manager-coach; they are mentioned here only so crews recognise the trap.