## Slide 1
Site Leadership Coach: Hazira gas terminal release and fire, 2020
Audience: T4 plant and asset leadership: the site leadership team
Incident: Hazira 2020 · 2020-09-24
Learning purposes: not a statutory document. Draft learnings from a ProbeMatrix investigation export; validate them before adoption. · Learnings drafted by an AI agent from AI-assisted findings
DRAFT
Review: draft · Classification: internal · Version 1.0
Draft because: the investigation status is in progress; no finding is marked as edited by a person
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Audience: T4 plant and asset leadership: the site leadership team
Incident: Hazira 2020 · 2020-09-24
Learning purposes: not a statutory document. Draft learnings from a ProbeMatrix investigation export; validate them before adoption. · Learnings drafted by an AI agent from AI-assisted findings
DRAFT
Review: draft · Classification: internal · Version 1.0
Draft because: the investigation status is in progress; no finding is marked as edited by a person
Data quality and limits:
- Draft learnings from an unreviewed analysis: the export's Investigation Status is in_progress and no finding is marked as edited by a person, so this pack stays a draft until the investigation is completed and reviewed.
- One source date conflicts: the gasket-history record quotes a change on 18/09/2019, while its own note and the narrative place the most recent change on 18-Sep-2020. The timeline keeps the 2020 date and leaves the 2019 entry out. [EVD-1494]

## Slide 2
Bottom line 1/4
The emergency plan gave the night shift no isolation criteria and no standing authority below the plant manager, so the decision to isolate travelled up a chain of phone calls while the cloud grew.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: The emergency plan gave the night shift no isolation criteria and no standing authority below the plant manager, so the decision to isolate travelled up a chain of phone calls while the cloud grew.
Cites: FND-82761CC5; FND-314D34C5; EVD-4052; EVD-3932
Cited records:
FND-82761CC5: No delegated authority or criteria for emergency isolation in DMP and night-shift structure · L4 · rating 4
FND-314D34C5: Control Room Operators - DMP Isolation Decision Criteria · L1 · rating 4
EVD-4052: document
EVD-3932: document

## Slide 3
Bottom line 2/4
Isolation and detection were set up so that someone had to reach the release: valves closed only by hand at the valve, and detection that only displayed an alarm.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Isolation and detection were set up so that someone had to reach the release: valves closed only by hand at the valve, and detection that only displayed an alarm.
Cites: FND-044D1DEC; FND-6155A1C2; EVD-3932; EVD-8657
Cited records:
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
FND-6155A1C2: F&G detection system had no auto-shutdown or fire-suppression interlock · L4 · rating 4
EVD-3932: document
EVD-8657: log_record

## Slide 4
Bottom line 3/4
Workarounds became normal because nothing on site stopped them: a substitute seal used as regular practice, return to service at operating pressure only, and electrical fittings repaired only on breakdown.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Workarounds became normal because nothing on site stopped them: a substitute seal used as regular practice, return to service at operating pressure only, and electrical fittings repaired only on breakdown.
Cites: FND-B440C1BF; FND-5919B328; FND-1280E788; EVD-8645; EVD-2894; EVD-6916
Cited records:
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
EVD-8645: document
EVD-2894: document
EVD-6916: physical_item

## Slide 5
Bottom line 4/4
Warnings were on record for years (repeat seal changes, pipe-wall loss, an unused change procedure), and none reached a leadership decision that changed the plant.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Warnings were on record for years (repeat seal changes, pipe-wall loss, an unused change procedure), and none reached a leadership decision that changed the plant.
Cites: FND-8083ECAC; FND-1A251687; FND-0F19C9FC; EVD-1494; EVD-5527; EVD-2986
Cited records:
FND-8083ECAC: MOC formal risk assessment not applied to the OEM-to-O-ring gasket substitution · L3 · rating 4
FND-1A251687: Chronic gasket failure on 310FT01 left to routine resealing — no OEM spares, root-cause or replacement programme · L4 · rating 4
FND-0F19C9FC: 2017 pipeline thickness-loss findings left unactioned for over three years · L4 · rating 3
EVD-1494: document
EVD-5527: document
EVD-2986: document

## Slide 6
Decisions for the leadership team
Give shift crews standing written authority to isolate and shut down on criteria written into the emergency plan
Options:
Shift in-charge isolates on defined criteria and reports afterwards
Control-room operator isolates on a confirmed release, shift in-charge confirms
Trade-offs: Delegation removes the escalation delay but means accepting some isolations that later prove unnecessary, with lost production; the leadership team has to back crews who isolate in good faith.
Owner: Operations function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Give shift crews standing written authority to isolate and shut down on criteria written into the emergency plan
Options:
- Shift in-charge isolates on defined criteria and reports afterwards
- Control-room operator isolates on a confirmed release, shift in-charge confirms
Trade-offs: Delegation removes the escalation delay but means accepting some isolations that later prove unnecessary, with lost production; the leadership team has to back crews who isolate in good faith.
Owner: Operations function
Cites: FND-82761CC5; FND-314D34C5; FND-AE629313; EVD-4052; FND-81E3EEA0; FND-500E0B2D; FND-8DAFDADC; FND-7505B1AF; FND-2EC435D0; FND-BB4CC662
Cited records:
FND-82761CC5: No delegated authority or criteria for emergency isolation in DMP and night-shift structure · L4 · rating 4
FND-314D34C5: Control Room Operators - DMP Isolation Decision Criteria · L1 · rating 4
FND-AE629313: Emergency isolation response - MOV 54 closure delay · L1 · rating 4
EVD-4052: document
FND-81E3EEA0: DMP/ERDMP hydrocarbon-leakage guidance omits isolation/stoppage decision criteria · L2 · rating 4
FND-500E0B2D: On-site DMP emergency response planning for hydrocarbon leakage · L2 · rating 4
FND-8DAFDADC: Emergency isolation authority not allocated to on-shift operators · L2 · rating 4
FND-7505B1AF: Steep authority gradient in emergency response · L2 · rating 4
FND-2EC435D0: DMP/ERDMP hydrocarbon-leak scenario lacked isolation/stoppage decision criteria · L3 · rating 4
FND-BB4CC662: Emergency isolation intent/criteria never communicated to night shift through DMP/standing orders · L3 · rating 4

## Slide 7
Decisions for the leadership team
Needs corporate decision: fund remote operation of the emergency isolation valves for inventories that can form a large vapour cloud
Options:
Remote operation from the control room
Automatic closure on confirmed gas detection where justified
Trade-offs: Remote operation is likely to need capital and a shutdown window; without it, isolation still depends on reaching the valve through the release.
Owner: Engineering function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Needs corporate decision: fund remote operation of the emergency isolation valves for inventories that can form a large vapour cloud
Options:
- Remote operation from the control room
- Automatic closure on confirmed gas detection where justified
Trade-offs: Remote operation is likely to need capital and a shutdown window; without it, isolation still depends on reaching the valve through the release.
Owner: Engineering function
Cites: FND-044D1DEC; FND-4C645CB5; FND-31405D96; EVD-3932; FND-A19F3D9C; FND-9B406A83; FND-594A80E9; FND-BDD73BA2; FND-FD0EF0F5
Cited records:
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
FND-4C645CB5: Emergency isolation MOVs not configured for remote operation from the control room · L2 · rating 4
FND-31405D96: Gas Terminal emergency isolation MOVs local-only, no remote operation from control room · L2 · rating 4
EVD-3932: document
FND-A19F3D9C: Emergency isolation capability and shift-authority planning · L2 · rating 3
FND-9B406A83: Condensate Vapour Cloud Obscuring Leak Source · L2 · rating 4
FND-594A80E9: GSP Shift In-charge and Overall Shift In-charge - 02:35-03:01 hrs · L2 · rating 4
FND-BDD73BA2: Vapour cloud density preventing personnel approach to leak source · L2 · rating 4
FND-FD0EF0F5: Gas Terminal CR Personnel - Vapour Cloud Visibility · L1 · rating 3

## Slide 8
Decisions for the leadership team
Needs corporate decision: approve fire and gas voting logic with automatic executive action for major-release areas
Options:
Automatic shutdown and protection on confirmed detection
Alarm with a timed operator action, backed by automatic action
Trade-offs: Automatic action brings spurious-trip risk and engineering cost; display-only detection left the response to a manual chain.
Owner: Engineering function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Needs corporate decision: approve fire and gas voting logic with automatic executive action for major-release areas
Options:
- Automatic shutdown and protection on confirmed detection
- Alarm with a timed operator action, backed by automatic action
Trade-offs: Automatic action brings spurious-trip risk and engineering cost; display-only detection left the response to a manual chain.
Owner: Engineering function
Cites: FND-6155A1C2; FND-4D7CF773; EVD-8657; FND-15B4E60F
Cited records:
FND-6155A1C2: F&G detection system had no auto-shutdown or fire-suppression interlock · L4 · rating 4
FND-4D7CF773: No policy required the F&G detection system to be interlocked to automatic plant shutdown and fire-suppression activation · L3 · rating 4
EVD-8657: log_record
FND-15B4E60F: Gas Terminal emergency operations workspace — display-only F&G, manual MOVs, single CCTV, no isolation criteria · L3 · rating 4

## Slide 9
Decisions for the leadership team
Give one function ownership of pressure-part specifications and of approving any substitute part
Options:
Engineering function owns specifications; stores issue only against them
Maintenance function owns them with engineering approval of substitutes
Trade-offs: One owner in engineering separates the person fitting the part from the person approving it, at the cost of an extra step for urgent repairs.
Owner: Engineering function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Give one function ownership of pressure-part specifications and of approving any substitute part
Options:
- Engineering function owns specifications; stores issue only against them
- Maintenance function owns them with engineering approval of substitutes
Trade-offs: One owner in engineering separates the person fitting the part from the person approving it, at the cost of an extra step for urgent repairs.
Owner: Engineering function
Cites: FND-B440C1BF; FND-DE30BD8B; EVD-8645
Cited records:
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-DE30BD8B: Management failed to provide any substitute-specification, procurement, or quality-control policy after the OEM gasket specification was lost · L3 · rating 4
EVD-8645: document

## Slide 10
Decisions for the leadership team
Treat return to service after pressure-boundary work as a hold point that operations accepts in writing against a test record
Options:
Hold point with a design-pressure test record
Hold point with an engineering-approved alternative test
Trade-offs: A hold point adds time before restart; without it the meter went back online after an operating-pressure soak only.
Owner: Operations function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Treat return to service after pressure-boundary work as a hold point that operations accepts in writing against a test record
Options:
- Hold point with a design-pressure test record
- Hold point with an engineering-approved alternative test
Trade-offs: A hold point adds time before restart; without it the meter went back online after an operating-pressure soak only.
Owner: Operations function
Cites: FND-5919B328; EVD-2894; EVD-0185
Cited records:
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
EVD-2894: document
EVD-0185: log_record

## Slide 11
Decisions for the leadership team
Fund replacement of old HPMV fittings in zoned areas with certified fittings, and move their maintenance from breakdown to planned inspection
Options:
Replace all fittings in the zoned areas in one programme
Inspect all now and replace on condition
Trade-offs: Full replacement costs more at once; inspect-and-replace leaves old fittings in service longer but finds the worst first.
Owner: Maintenance function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Fund replacement of old HPMV fittings in zoned areas with certified fittings, and move their maintenance from breakdown to planned inspection
Options:
- Replace all fittings in the zoned areas in one programme
- Inspect all now and replace on condition
Trade-offs: Full replacement costs more at once; inspect-and-replace leaves old fittings in service longer but finds the worst first.
Owner: Maintenance function
Cites: FND-1280E788; EVD-6916; EVD-0496
Cited records:
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
EVD-6916: physical_item
EVD-0496: photograph

## Slide 12
Decisions for the leadership team
Allow no extension of a safety recommendation without the documented approval the procedure requires, and review overdue items monthly
Options:
Monthly review by the leadership team
Quarterly review with escalation of any unapproved extension
Trade-offs: A monthly review takes leadership time; the evidence shows extensions ran without the required approval.
Owner: HSE and process safety function
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: Decision: Allow no extension of a safety recommendation without the documented approval the procedure requires, and review overdue items monthly
Options:
- Monthly review by the leadership team
- Quarterly review with escalation of any unapproved extension
Trade-offs: A monthly review takes leadership time; the evidence shows extensions ran without the required approval.
Owner: HSE and process safety function
Cites: FND-850B270C; FND-5A742738; EVD-6852
Cited records:
FND-850B270C: External safety audit recommendations overdue without required approval for extensions · L3 · rating 2
FND-5A742738: External Safety Audit February 2018 recommendations overdue with extension dates lacking documented competent-authority approval · L3 · rating 2
EVD-6852: document

## Slide 13
How the site set this up
The maintenance and spares programme, one of the two largest hubs in the causal links, did not supply a specification for the 1986 meter's gasket or a reliability review of…
A culture that allowed unsafe work and applied risk management unevenly leads to gaps in the guidance supervisors gave and to routine deviations at the job. The findings read…
Command and control resources and the timing of upgrades lead to equipment that was not set up for an emergency and to automation that was not provided. The isolation valves had…
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. The maintenance and spares programme, one of the two largest hubs in the causal links, did not supply a specification for the 1986 meter's gasket or a reliability review of…
Text: The maintenance and spares programme, one of the two largest hubs in the causal links, did not supply a specification for the 1986 meter's gasket or a reliability review of repeat failures. Supervision therefore could not act on the risk it saw, rules on the job were not enforced, and checklists were not followed at return to service. The pathway ends on a seal that was not to specification and was never tested to design pressure [FND-1A251687; FND-B440C1BF; FND-5919B328; EVD-8645; EVD-2894].
Cites: FND-1A251687; FND-B440C1BF; FND-5919B328; EVD-8645; EVD-2894; FND-DE30BD8B; FND-F0D015E1
2. A culture that allowed unsafe work and applied risk management unevenly leads to gaps in the guidance supervisors gave and to routine deviations at the job. The findings read…
Text: A culture that allowed unsafe work and applied risk management unevenly leads to gaps in the guidance supervisors gave and to routine deviations at the job. The findings read this as norms, not choices by one person: the substitute O-ring was 'regular practice', and the change procedure was not used after 2018. The pathway ends on changes to the plant that nobody reviewed [FND-8083ECAC; FND-B440C1BF; EVD-2986; EVD-8645].
Cites: FND-8083ECAC; FND-B440C1BF; EVD-2986; EVD-8645; FND-ADF96860; FND-07080447; FND-6ECCE231; FND-9F8CA896; FND-922A04DB
3. Command and control resources and the timing of upgrades lead to equipment that was not set up for an emergency and to automation that was not provided. The isolation valves had…
Text: Command and control resources and the timing of upgrades lead to equipment that was not set up for an emergency and to automation that was not provided. The isolation valves had no remote operation and the fire and gas system had no executive action. The pathway ends on an isolation that depended on people reaching the valve through the cloud [FND-044D1DEC; FND-6155A1C2; FND-9B406A83; EVD-3932].
Cites: FND-044D1DEC; FND-6155A1C2; FND-9B406A83; EVD-3932; FND-4C645CB5; FND-31405D96; FND-A19F3D9C; FND-594A80E9; FND-BDD73BA2; FND-FD0EF0F5
Cited records:
FND-1A251687: Chronic gasket failure on 310FT01 left to routine resealing — no OEM spares, root-cause or replacement programme · L4 · rating 4
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
EVD-8645: document
EVD-2894: document
FND-DE30BD8B: Management failed to provide any substitute-specification, procurement, or quality-control policy after the OEM gasket specification was lost · L3 · rating 4
FND-F0D015E1: No formal risk assessment following the recurrent gasket failure pattern · L3 · rating 3
FND-8083ECAC: MOC formal risk assessment not applied to the OEM-to-O-ring gasket substitution · L3 · rating 4
EVD-2986: document
FND-ADF96860: MOC SOP published 2016 but not implemented since 2018 · L3 · rating 3
FND-07080447: Management of Change - zero MOCs implemented since 2018 · L3 · rating 3
FND-6ECCE231: Management of Change policy published in August 2016 was not implemented, with no MOCs since 2018 · L3 · rating 3
FND-9F8CA896: Management of Change SOP published Aug-2016 not enforced — zero MOCs since 2018 · L3 · rating 3
FND-922A04DB: Management of Change (MOC) programme published but not implemented since 2018 · L4 · rating 3
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
FND-6155A1C2: F&G detection system had no auto-shutdown or fire-suppression interlock · L4 · rating 4
FND-9B406A83: Condensate Vapour Cloud Obscuring Leak Source · L2 · rating 4
EVD-3932: document
FND-4C645CB5: Emergency isolation MOVs not configured for remote operation from the control room · L2 · rating 4
FND-31405D96: Gas Terminal emergency isolation MOVs local-only, no remote operation from control room · L2 · rating 4
FND-A19F3D9C: Emergency isolation capability and shift-authority planning · L2 · rating 3
FND-594A80E9: GSP Shift In-charge and Overall Shift In-charge - 02:35-03:01 hrs · L2 · rating 4
FND-BDD73BA2: Vapour cloud density preventing personnel approach to leak source · L2 · rating 4
FND-FD0EF0F5: Gas Terminal CR Personnel - Vapour Cloud Visibility · L1 · rating 3

## Slide 14
Signals that reached leadership
Timeline: 10 entries
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Timeline: 10 entries
- c. 2011 (about 9 years before): chedule for thickness measurement is every four years... As per the records, the last two thickness measurement exercise was carried out in 2011 and 2017 which suggests that the schedule of four years is not being adhered to strictly" (p.29 [EVD-8307; FND-10FEDDD8; FND-5ABEE30B; FND-6FA2CEDE; FND-75CEBE09; FND-A3DCEBD8; FND-B8E1F804; FND-C4842890; FND-E87DC506; FND-F9D69EC8; FND-FCCB9505]
- 2016-08 (49 months before): gs for OEM rectangular-slot gaskets on meter 310FT01. [EVD-2986] documents that 'Management of Change (MOC) philosophy/SOP was published in August 2016. However, the procedure indicated in the document is not implemented while carrying out [EVD-2986; FND-07080447; FND-3FEE59DF; FND-6ECCE231; FND-7838175A; FND-922A04DB; FND-9F8CA896; FND-ADF96860; FND-CDE8E62D; FND-EB48C68C; FND-EEC2407A; FND-F7FE8463]
- c. 2018 (about 2 years before): cument is not implemented while carrying out change of Low-Pressure Gas to Kribhico from Medium Pressure Gas headers in LPG Plant in 2013 & 2018. It is informed no more MOCs are implemented in the plant since 2018.' The MOC SOP existed sinc [EVD-2986; FND-07080447; FND-3FEE59DF; FND-6ECCE231; FND-7838175A; FND-922A04DB; FND-9F8CA896; FND-ADF96860; FND-CDE8E62D; FND-EB48C68C; FND-EEC2407A; FND-F7FE8463]
- 2018-11 (22 months before): nted recurrence of sealing failures. [EVD-1494] records that "Cleaning/servicing/calibration of meters 1 & 2 was carried out on 12th & 13th Nov 2018. Afterwards, meter no.1 was cleaned on 25/02/2019 & gasket was changed. Again on 18/09/2019 [EVD-1494; FND-065439DE; FND-110F964C; FND-1A251687; FND-350C35AD; FND-3A34BAD3; FND-4EDE038A; FND-54180594; FND-55F68376; FND-69067A1C; FND-71D631C1; FND-82FC718D; FND-8B4A5414; FND-A3D7D53F; FND-AC8FBB26; FND-B86F67F0; FND-CEE3D4D7; FND-D14B8424; FND-E0AE86A6; FND-F0D015E1; FND-FEC84761]
- 2019-02-25 (18 months before): records that "Cleaning/servicing/calibration of meters 1 & 2 was carried out on 12th & 13th Nov 2018. Afterwards, meter no.1 was cleaned on 25/02/2019 & gasket was changed. Again on 18/09/2019, gasket was changed which leaked within one yea [EVD-1494; FND-065439DE; FND-110F964C; FND-1A251687; FND-350C35AD; FND-3A34BAD3; FND-4EDE038A; FND-54180594; FND-55F68376; FND-69067A1C; FND-71D631C1; FND-82FC718D; FND-8B4A5414; FND-A3D7D53F; FND-AC8FBB26; FND-B86F67F0; FND-CEE3D4D7; FND-D14B8424; FND-E0AE86A6; FND-F0D015E1; FND-FEC84761]
- 2019-07 (14 months before): thickness of 1.03mm along with heavy pitting and painting peeling off was observed in one of the segments of 36 pipeline in gas terminal in July 2019. The corrective action of painting was completed in Dec. 2019. However, as per the availab [EVD-2397; FND-159C9FD7; FND-20034564; FND-4722A2B8; FND-4DAC9500; FND-6E13192C; FND-7D59D47D; FND-8EFDE3D9; FND-999326F0; FND-ABDADA0C; FND-B2B200D4; FND-B412FF47; FND-B5D6A73E; FND-C90FA7A2; FND-E5C4209D; FND-FA73D914]
- 2019-12 (9 months before): evealed '1.03mm thickness reduction along with heavy pitting and painting peeling off... The corrective action of painting was completed in Dec. 2019. However, as per the available data, the design thickness of the pipeline is 23.83mm with [EVD-2397; FND-159C9FD7; FND-20034564; FND-4722A2B8; FND-4DAC9500; FND-5EC15274; FND-6E13192C; FND-8EFDE3D9; FND-999326F0; FND-ABDADA0C; FND-B2B200D4; FND-B412FF47; FND-B5D6A73E; FND-C90FA7A2; FND-E5C4209D; FND-FA73D914]
- 2019-12-18 (9 months before): without documentation violated fundamental calibration management principles. [EVD-2506] documents: 'During calibration from 17/12/2019 to 18/12/2019, calibration was changed from 16000 mmwc to 2540 mmwc for 310FT01 without any mention of t [EVD-2506; FND-0B651843; FND-0BA85877; FND-13E2037D; FND-403FD778; FND-6381588B; FND-693FEDD2; FND-7C8ADD7C; FND-7F829BEB; FND-85748D86; FND-89A8965A; FND-89D53630; FND-8D744668; FND-98F7C845; FND-A534A1C3; FND-B0BA0566; FND-C2B4989C; FND-E94D563C; FND-FD98468B]
- 2020-09-17: ble individual, resulting in open notifications and missing post-job reviews. [EVD-0591] states: 'Notification no. 3800419840 was raised on 17/09/2020 for malfunction of meter no.1… Notification was not closed after completion of the job' ( [EVD-0591; FND-267F1E09; FND-2B53492C; FND-30C43927; FND-55F68376; FND-62EF1667; FND-678E51A3; FND-6D3446CD; FND-8071945B; FND-96DB7E93; FND-977FABA2; FND-AE60859C; FND-C59DCD29; FND-FA807C69]
- 2020-09-18: testing of pressure boundaries after maintenance. [EVD-2894] documents: 'After calibration of the meter 310FE01, the gasket was replaced on 18.09.2020. No hydro test was done after replacement of the gasket. The system was only pressurised [EVD-2894; FND-137BC719; FND-1662466D; FND-257C1100; FND-3AB996FC; FND-491EDE74; FND-4944554C; FND-50C7319E; FND-5919B328; FND-611A8BFC; FND-615DB819; FND-7C5ED5B3; FND-7FA02383; FND-8ACDE078; FND-904FCA63; FND-A3D7D53F; FND-C4E06264; FND-FDFA6FF5]
Cites: EVD-8307; FND-10FEDDD8; FND-5ABEE30B; FND-6FA2CEDE; FND-75CEBE09; FND-A3DCEBD8; FND-B8E1F804; FND-C4842890; FND-E87DC506; FND-F9D69EC8; FND-FCCB9505; EVD-2986; FND-07080447; FND-3FEE59DF; FND-6ECCE231; FND-7838175A; FND-922A04DB; FND-9F8CA896; FND-ADF96860; FND-CDE8E62D; FND-EB48C68C; FND-EEC2407A; FND-F7FE8463; EVD-1494; FND-065439DE; FND-110F964C; FND-1A251687; FND-350C35AD; FND-3A34BAD3; FND-4EDE038A; FND-54180594; FND-55F68376; FND-69067A1C; FND-71D631C1; FND-82FC718D; FND-8B4A5414; FND-A3D7D53F; FND-AC8FBB26; FND-B86F67F0; FND-CEE3D4D7; FND-D14B8424; FND-E0AE86A6; FND-F0D015E1; FND-FEC84761; EVD-2397; FND-159C9FD7; FND-20034564; FND-4722A2B8; FND-4DAC9500; FND-6E13192C; FND-7D59D47D; FND-8EFDE3D9; FND-999326F0; FND-ABDADA0C; FND-B2B200D4; FND-B412FF47; FND-B5D6A73E; FND-C90FA7A2; FND-E5C4209D; FND-FA73D914; FND-5EC15274; EVD-2506; FND-0B651843; FND-0BA85877; FND-13E2037D; FND-403FD778; FND-6381588B; FND-693FEDD2; FND-7C8ADD7C; FND-7F829BEB; FND-85748D86; FND-89A8965A; FND-89D53630; FND-8D744668; FND-98F7C845; FND-A534A1C3; FND-B0BA0566; FND-C2B4989C; FND-E94D563C; FND-FD98468B; EVD-0591; FND-267F1E09; FND-2B53492C; FND-30C43927; FND-62EF1667; FND-678E51A3; FND-6D3446CD; FND-8071945B; FND-96DB7E93; FND-977FABA2; FND-AE60859C; FND-C59DCD29; FND-FA807C69; EVD-2894; FND-137BC719; FND-1662466D; FND-257C1100; FND-3AB996FC; FND-491EDE74; FND-4944554C; FND-50C7319E; FND-5919B328; FND-611A8BFC; FND-615DB819; FND-7C5ED5B3; FND-7FA02383; FND-8ACDE078; FND-904FCA63; FND-C4E06264; FND-FDFA6FF5
Cited records:
EVD-8307: document
FND-10FEDDD8: Four-year pipeline thickness measurement schedule and 2017 corrective actions not enforced · L3 · rating 3
FND-5ABEE30B: Four-year pipeline thickness-monitoring schedule not adhered to and not restored to compliance · L3 · rating 2
FND-6FA2CEDE: Four-year UT thickness-measurement schedule breached (2011→2017 gap of 6 years) with no supervisory enforcement · L3 · rating 2
FND-75CEBE09: Four-year thickness measurement schedule not enforced · L3 · rating 2
FND-A3DCEBD8: Pipeline thickness-monitoring programme off cadence and 2017 corrective-action findings left unplanned for 3+ years · L4 · rating 3
FND-B8E1F804: Mandated four-year thickness measurement cadence breached · L4 · rating 2
FND-C4842890: Mandated four-year UT thickness inspection cadence breached · L4 · rating 2
FND-E87DC506: Pipeline thickness measurement schedule and 2017 corrective actions not completed · L2 · rating 2
FND-F9D69EC8: Pipeline thickness-measurement schedule programme not enforced (2011 to 2017 gap) · L4 · rating 2
FND-FCCB9505: Pipeline thickness measurement schedule not enforced for gas-terminal trunk lines · L3 · rating 2
EVD-2986: document
FND-07080447: Management of Change - zero MOCs implemented since 2018 · L3 · rating 3
FND-3FEE59DF: MOC procedure published August 2016 but not implemented since 2018 · L4 · rating 3
FND-6ECCE231: Management of Change policy published in August 2016 was not implemented, with no MOCs since 2018 · L3 · rating 3
FND-7838175A: Maintenance Planners - MOC Policy for Gasket Specification Changes · L1 · rating 3
FND-922A04DB: Management of Change (MOC) programme published but not implemented since 2018 · L4 · rating 3
FND-9F8CA896: Management of Change SOP published Aug-2016 not enforced — zero MOCs since 2018 · L3 · rating 3
FND-ADF96860: MOC SOP published 2016 but not implemented since 2018 · L3 · rating 3
FND-CDE8E62D: Management of Change SOP not implemented since 2018, leaving the gasket substitution outside engineering review · L3 · rating 3
FND-EB48C68C: MOC policy published but not implemented since 2018 · L3 · rating 3
FND-EEC2407A: Plant-wide suspension of MOC exemplified by the 2013/2018 LP-to-Kribhico header change · L4 · rating 2
FND-F7FE8463: Management of Change policy not implemented since 2018, allowing unapproved material substitution · L4 · rating 4
EVD-1494: document
FND-065439DE: Recurring gasket-failure pattern on meter 310FT01 not escalated for root-cause action · L3 · rating 3
FND-110F964C: Maintenance supervision failed to act on the recurring gasket-failure pattern on meter 310FT01 (12-Nov-2018, 25-Feb-2019, 18-Sep-2020) · L3 · rating 4
FND-1A251687: Chronic gasket failure on 310FT01 left to routine resealing — no OEM spares, root-cause or replacement programme · L4 · rating 4
FND-350C35AD: Three gasket replacements in 22 months without root-cause investigation or engineering review · L2 · rating 3
FND-3A34BAD3: Meter 310FT01 gasket replacement recurrence treated as routine maintenance · L4 · rating 4
FND-4EDE038A: Recurrent 310FT01 gasket failures - no supervisory root-cause response · L3 · rating 4
FND-54180594: Maintenance crew unfamiliar with OEM rectangular-slot gasket specification - Sep 2020 replacement · L2 · rating 4
FND-55F68376: Meter 310FT01 kept in service despite three gasket failures in 22 months and a 1986-vintage pressure boundary · L4 · rating 4
FND-69067A1C: Chronically failing meter 310FT01 kept in service across three gasket replacements in 22 months · L2 · rating 4
FND-71D631C1: Recurrent gasket failure pattern on 310FT01 not root-caused or corrected · L3 · rating 4
FND-82FC718D: Recurring gasket failures on 310FT01 treated as routine maintenance instead of reliability warning · L4 · rating 4
FND-8B4A5414: Recurring gasket failures on 310FT01 not escalated to root-cause analysis, re-engineering, or meter replacement · L3 · rating 3
FND-A3D7D53F: Maintenance crew authorised for the 18-Sep-2020 retaining-plate gasket replacement without OEM specification or pressure-boundary testing competence · L3 · rating 4
FND-AC8FBB26: Reliability planning failure across the 22-month gasket replacement history · L2 · rating 3
FND-B86F67F0: Regular use of locally procured O-rings for the 1986 rectangular-slot meter gasket · L4 · rating 4
FND-CEE3D4D7: Recurrent meter 310FT01 gasket failures addressed by repeating the same inadequate O-ring fix · L3 · rating 4
FND-D14B8424: Maintenance leadership - 22-month recurring gasket-failure pattern not escalated · L3 · rating 4
FND-E0AE86A6: Recurrent gasket-failure program risk on meter 310FT01 never assessed · L4 · rating 4
FND-F0D015E1: No formal risk assessment following the recurrent gasket failure pattern · L3 · rating 3
FND-FEC84761: Three gasket failures in 22 months on meter 310FT01 — recurrent identified risk with no root-cause investigation or mitigation · L3 · rating 4
EVD-2397: document
FND-159C9FD7: Supervision accepted painting-only corrective action for the July 2019 1.03 mm pitting/zero-corrosion-allowance finding on the 36-inch pipeline · L3 · rating 2
FND-20034564: July 2019 1.03 mm pitting finding accepted with painting-only corrective action · L3 · rating 3
FND-4722A2B8: July 2019 pitting/thickness loss on 36-inch line addressed with painting only, with no supervisory review of remedial adequacy · L3 · rating 3
FND-4DAC9500: 1.03 mm wall loss with heavy pitting on zero-corrosion-allowance 36-inch segment remediated with painting only · L4 · rating 3
FND-6E13192C: Painting-only corrective action accepted for pitted zero-corrosion-allowance 36-inch pipeline segment · L4 · rating 3
FND-7D59D47D: Program risk of zero-corrosion-allowance pitting addressed by painting only · L4 · rating 2
FND-8EFDE3D9: July 2019 pitting on 36″ gas-terminal pipeline — identified 1.03 mm loss on a zero-corrosion-allowance line mitigated only by painting · L3 · rating 3
FND-999326F0: Zero-corrosion-allowance 36-inch segment with 1.03 mm pitting only painted, not removed or replaced · L4 · rating 2
FND-ABDADA0C: Authorised painting-only remedy for corroded zero-corrosion-allowance pipeline · L3 · rating 3
FND-B2B200D4: July 2019 pitting on the 36-inch pipeline addressed only by painting, an inadequate mitigation for metal loss · L3 · rating 3
FND-B412FF47: Overconfidence in a pitted zero-corrosion-allowance 36-inch pipeline segment after painting-only correction · L4 · rating 3
FND-B5D6A73E: Pipeline-integrity decision oversight - painting-only remedy on 1.03 mm loss · L3 · rating 3
FND-C90FA7A2: 1.03 mm wall loss and pitting on zero-corrosion-allowance 36-inch pipe remediated only by painting · L3 · rating 2
FND-E5C4209D: July 2019 pitting and 1.03 mm loss on zero-allowance 36-inch line treated with painting only · L3 · rating 3
FND-FA73D914: 36-inch pipeline pitting and 1.03 mm metal loss addressed by painting only · L4 · rating 3
FND-5EC15274: July 2019 - Wrong Choice: Painting Only for 1.03mm Thickness Loss with Zero Corrosion Allowance · L1 · rating 3
EVD-2506: log_record
FND-0B651843: Calibration programme executed without checklist or recorded setpoint change on meter 310FT01 (Dec-2019) · L4 · rating 3
FND-0BA85877: Undocumented calibration setting changes on critical meters · L1 · rating 3
FND-13E2037D: Meter 310FT01 calibration setting changed from 16000 to 2540 mmwc in Dec-2019 without documentation or checklist · L2 · rating 3
FND-403FD778: Calibration documentation and checklist rules not enforced during Dec-2019 calibration of 310FT01 · L3 · rating 3
FND-6381588B: Calibration team cross-monitoring failure — December 2019 undocumented setpoint change · L2 · rating 3
FND-693FEDD2: Calibration setpoint changes on 310FT01 (16000→2540→16000 mmwc) left uncorrected and undocumented by supervision · L3 · rating 3
FND-7C8ADD7C: Dec-2019 calibration team lacked independent verifier and checklist discipline · L3 · rating 3
FND-7F829BEB: December 2019 calibration setpoint changes undocumented and checklist-free · L4 · rating 3
FND-85748D86: Maintenance Team - Undocumented Calibration Change Dec 2019 · L1 · rating 3
FND-89A8965A: Calibration record-keeping on meter 310FT01 — no standardized checklist or documentation rule · L3 · rating 3
FND-89D53630: Instrument/calibration supervision - Dec-2019 unsigned setpoint change · L3 · rating 3
FND-8D744668: Calibration team - Dec 2019 setpoint change not communicated · L2 · rating 3
FND-98F7C845: No calibration checklist for critical high-pressure meter work · L4 · rating 3
FND-A534A1C3: Calibration crew authorised for Dec-2019 high-pressure calibration of meter 310FT01 without checklist or documentation discipline · L3 · rating 3
FND-B0BA0566: Unmanaged setpoint change on meter 310FT01 during December 2019 calibration · L4 · rating 3
FND-C2B4989C: Calibration work on 310FT01 — no checklist followed and undocumented setpoint changes in Dec 2019 · L2 · rating 3
FND-E94D563C: Calibration setpoint change 16000 to 2540 mmwc not communicated in signed records · L3 · rating 3
FND-FD98468B: Undocumented calibration setpoint changes with no checklist on meter 310FT01 · L4 · rating 3
EVD-0591: log_record
FND-267F1E09: SAP Notification 3800419840 not closed or supervisor-reviewed after the gasket job · L2 · rating 3
FND-2B53492C: SAP Notification 3800419840 left open with no supervisory closure review after the meter repair · L3 · rating 3
FND-30C43927: SAP maintenance notification closure programme: notification 3800419840 not closed or reviewed · L4 · rating 3
FND-62EF1667: SAP Notification 3800419840 left open and unreviewed · L4 · rating 3
FND-678E51A3: SAP maintenance-work closure loop broken — notification 3800419840 never closed or reviewed · L4 · rating 3
FND-6D3446CD: SAP notification closure review after 18-Sep-2020 job not enforced · L3 · rating 3
FND-8071945B: SAP Notification 3800419840 not closed - no completion feedback loop · L2 · rating 3
FND-96DB7E93: SAP notification closure oversight - 3800419840 left open · L3 · rating 3
FND-977FABA2: SAP Notification 3800419840 left open with no supervisory closure review · L3 · rating 3
FND-AE60859C: SAP notification 3800419840 left unclosed without supervisory review · L3 · rating 3
FND-C59DCD29: SAP notification closure responsibility not defined · L2 · rating 3
FND-FA807C69: SAP notification 3800419840 for meter 310FT01 was never closed or reviewed by supervision after the 18-Sep-2020 job · L3 · rating 3
EVD-2894: document
FND-137BC719: No SOP for calibration and return-to-service of high-pressure meters · L3 · rating 4
FND-1662466D: Meter 310FT01 returned to service with locally sourced substitute O-ring gasket and no hydrotest · L2 · rating 4
FND-257C1100: No standard operating procedure existed for calibration and return-to-service of the high-pressure meters, including mandatory hydrotest to design pressure · L3 · rating 4
FND-3AB996FC: Return-to-service after gasket replacement without design-pressure hydrostatic test · L4 · rating 4
FND-491EDE74: Return of meter 310FT01 to service after 18-Sep-2020 gasket change without design-pressure validation · L4 · rating 4
FND-4944554C: Pressure boundary work returned to service without hydrostatic test · L1 · rating 4
FND-50C7319E: No post-maintenance hydrotest or return-to-service SOP for high-pressure meter gasket work · L4 · rating 4
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
FND-611A8BFC: Omitted hydrostatic test and absence of SOP for high-pressure meter return-to-service · L3 · rating 4
FND-615DB819: Maintenance job manning for the 18-Sep-2020 gasket replacement · L4 · rating 4
FND-7C5ED5B3: Maintenance Team - Hydrostatic Test Requirement After Gasket Replacement · L1 · rating 4
FND-7FA02383: Post-Maintenance Gasket Replacement - 18-Sep-2020 · L1 · rating 4
FND-8ACDE078: Omission of post-replacement hydrostatic test not identified or corrected before meter return to service · L3 · rating 4
FND-904FCA63: Failure to enforce hydrostatic test and return-to-service SOP after gasket replacement · L3 · rating 4
FND-C4E06264: Post-repair hydrostatic test requirement not enforced on 18-Sep-2020 gasket replacement · L3 · rating 4
FND-FDFA6FF5: No hydrostatic test performed after the 18-Sep-2020 gasket replacement · L2 · rating 4

## Slide 15
Culture signals
Fitting a locally bought O-ring to a rectangular-slot flange was described as regular practice, repeated across three replacements in about 22 months, with no specification…
Breakdown repair was the accepted approach for flameproof fittings in the Zone 1 area, and twelve external-audit recommendations ran on extended dates with no record of the…
The emergency structure ran as a serial chain: perimeter security, CCTV room, gas terminal control room, shift in-charge, overall shift in-charge, then plant leadership. No role…
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Fitting a locally bought O-ring to a rectangular-slot flange was described as regular practice, repeated across three replacements in about 22 months, with no specification…
Text: Fitting a locally bought O-ring to a rectangular-slot flange was described as regular practice, repeated across three replacements in about 22 months, with no specification, quality check or recorded decision. Accepting a repaired pressure boundary after an operating-pressure soak had also become the modelled return-to-service practice [FND-B440C1BF; FND-A443D288; FND-71EE9734; EVD-8645; EVD-1494].
Cites: FND-B440C1BF; FND-A443D288; FND-71EE9734; EVD-8645; EVD-1494
2. Breakdown repair was the accepted approach for flameproof fittings in the Zone 1 area, and twelve external-audit recommendations ran on extended dates with no record of the…
Text: Breakdown repair was the accepted approach for flameproof fittings in the Zone 1 area, and twelve external-audit recommendations ran on extended dates with no record of the approval the procedure required. Both were visible in site records [FND-1280E788; FND-856F80CE; EVD-6916; EVD-6852].
Cites: FND-1280E788; FND-856F80CE; EVD-6916; EVD-6852
3. The emergency structure ran as a serial chain: perimeter security, CCTV room, gas terminal control room, shift in-charge, overall shift in-charge, then plant leadership. No role…
Text: The emergency structure ran as a serial chain: perimeter security, CCTV room, gas terminal control room, shift in-charge, overall shift in-charge, then plant leadership. No role below the plant manager held standing authority to close the isolation valve, so each step reported up rather than acted [FND-82761CC5; FND-A206DFD6; FND-4245FBF2; EVD-3932; EVD-6414].
Cites: FND-82761CC5; FND-A206DFD6; FND-4245FBF2; EVD-3932; EVD-6414
Cited records:
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-A443D288: O-ring substitution - regular practice tolerated and modelled by supervisors · L3 · rating 4
FND-71EE9734: Post-maintenance testing shortcut - operating-pressure-only modelled as the norm · L3 · rating 4
EVD-8645: document
EVD-1494: document
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
FND-856F80CE: 12 external-audit recommendations overdue without Director Offshore approval · L4 · rating 2
EVD-6916: physical_item
EVD-6852: document
FND-82761CC5: No delegated authority or criteria for emergency isolation in DMP and night-shift structure · L4 · rating 4
FND-A206DFD6: Serial management escalation and formal SIC-to-CIC hand-off design · L4 · rating 3
FND-4245FBF2: Night-shift senior leaders - delayed isolation at Gas Terminal Gate · L3 · rating 4
EVD-3932: document
EVD-6414: log_record

## Slide 16
Decisions for the leadership team
Time to isolation in drills
Remotely operable isolation
Detection with executive action
Parts issued against a specification
Restarts with a test record
Hazardous-area fittings inspected
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Time to isolation in drills
Indicator: Time to isolation in drills
Measure: Time from a confirmed release to first isolation in each emergency drill
Deterioration looks like: A drill in which isolation waits for a call above the shift in-charge
Owner: Operations function
Cites: FND-81E3EEA0; FND-500E0B2D; EVD-6414
2. Remotely operable isolation
Indicator: Remotely operable isolation
Measure: Share of emergency isolation valves on large inventories that can be closed from the control room
Deterioration looks like: No change over two quarters once funding is decided
Owner: Engineering function
Cites: FND-9B406A83; FND-044D1DEC; EVD-3932
3. Detection with executive action
Indicator: Detection with executive action
Measure: Share of major-release areas whose fire and gas detection triggers a defined executive action, proven in the last function test
Deterioration looks like: Any major-release area still display-only with no recorded decision
Owner: Engineering function
Cites: FND-15B4E60F; EVD-8657
4. Parts issued against a specification
Indicator: Parts issued against a specification
Measure: Share of pressure-boundary seals issued from stores with a specification reference
Deterioration looks like: Any seal issued without one
Owner: Engineering function
Cites: FND-B440C1BF; EVD-8645
5. Restarts with a test record
Indicator: Restarts with a test record
Measure: Share of pressure-boundary jobs returned to service with a signed test record
Deterioration looks like: Any restart without one
Owner: Operations function
Cites: FND-5919B328; EVD-2894
6. Hazardous-area fittings inspected
Indicator: Hazardous-area fittings inspected
Measure: Share of zoned-area light fittings with a recorded inspection in the planned interval
Deterioration looks like: Any fitting found with missing fasteners or an open enclosure
Owner: Maintenance function
Cites: FND-1280E788; EVD-6916
Cited records:
FND-81E3EEA0: DMP/ERDMP hydrocarbon-leakage guidance omits isolation/stoppage decision criteria · L2 · rating 4
FND-500E0B2D: On-site DMP emergency response planning for hydrocarbon leakage · L2 · rating 4
EVD-6414: log_record
FND-9B406A83: Condensate Vapour Cloud Obscuring Leak Source · L2 · rating 4
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
EVD-3932: document
FND-15B4E60F: Gas Terminal emergency operations workspace — display-only F&G, manual MOVs, single CCTV, no isolation criteria · L3 · rating 4
EVD-8657: log_record
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
EVD-8645: document
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
EVD-2894: document
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
EVD-6916: physical_item

## Slide 17
Decisions for the leadership team (continued)
Extensions with recorded approval
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 7. Extensions with recorded approval
Indicator: Extensions with recorded approval
Measure: Share of extended safety recommendations with the approval on file
Deterioration looks like: Any extension without it
Owner: HSE and process safety function
Cites: FND-850B270C; EVD-6852
Cited records:
FND-850B270C: External safety audit recommendations overdue without required approval for extensions · L3 · rating 2
EVD-6852: document

## Slide 18
What leaders will do visibly
Walk the metering area and the zoned lighting with the maintenance and electrical supervisors; ask to see the specification for one pressure seal and the inspection record for…
In every operations review, ask how many management-of-change records were raised this month and which field changes they cover.
Stop accepting a return to service after pressure-boundary work without a signed test record.
Stop accepting an extended safety recommendation without the approval the procedure requires.
Tell each shift, in person, that an isolation made in good faith on the plan's criteria will be backed, and attend the next emergency drill.
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Walk the metering area and the zoned lighting with the maintenance and electrical supervisors; ask to see the specification for one pressure seal and the inspection record for…
Text: Walk the metering area and the zoned lighting with the maintenance and electrical supervisors; ask to see the specification for one pressure seal and the inspection record for one flameproof fitting.
When: next 30 days
Cites: FND-B440C1BF; FND-1280E788; EVD-8645; EVD-6916
2. In every operations review, ask how many management-of-change records were raised this month and which field changes they cover.
Text: In every operations review, ask how many management-of-change records were raised this month and which field changes they cover.
When: next 30 days
Cites: FND-8083ECAC; EVD-2986
3. Stop accepting a return to service after pressure-boundary work without a signed test record.
Text: Stop accepting a return to service after pressure-boundary work without a signed test record.
When: next 30 days
Cites: FND-5919B328; EVD-2894
4. Stop accepting an extended safety recommendation without the approval the procedure requires.
Text: Stop accepting an extended safety recommendation without the approval the procedure requires.
When: next 30 days
Cites: FND-850B270C; EVD-6852
5. Tell each shift, in person, that an isolation made in good faith on the plan's criteria will be backed, and attend the next emergency drill.
Text: Tell each shift, in person, that an isolation made in good faith on the plan's criteria will be backed, and attend the next emergency drill.
When: next 30 days
Cites: FND-82761CC5; FND-314D34C5; EVD-4052
Cited records:
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
EVD-8645: document
EVD-6916: physical_item
FND-8083ECAC: MOC formal risk assessment not applied to the OEM-to-O-ring gasket substitution · L3 · rating 4
EVD-2986: document
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
EVD-2894: document
FND-850B270C: External safety audit recommendations overdue without required approval for extensions · L3 · rating 2
EVD-6852: document
FND-82761CC5: No delegated authority or criteria for emergency isolation in DMP and night-shift structure · L4 · rating 4
FND-314D34C5: Control Room Operators - DMP Isolation Decision Criteria · L1 · rating 4
EVD-4052: document

## Slide 19
Leadership workshop agenda (two hours)
Table: Time, Activity, Built on
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: 1. Table: Time, Activity, Built on
Columns:
- Time
- Activity
- Built on
Rows:
- 0:00-0:15 | Purpose and ground rules: learning, not blame; roles, not names | Status line and culture signals
- 0:15-0:40 | Walk the causal map: which hubs sit with this team | How the site set this up
- 0:40-1:05 | What had become normal, and what the team tolerated without seeing it | Culture signals
- 1:05-1:45 | Take the decisions: options, trade-offs and the owning function; mark what needs corporate decision | Decisions for the leadership team
- 1:45-2:00 | Agree the visible actions for the next 30 days and the indicators to review | Decisions and visible actions
Cites: FND-B440C1BF; FND-1A251687; FND-6155A1C2; FND-A443D288; FND-1280E788; FND-82761CC5; FND-044D1DEC; FND-5919B328; FND-850B270C
Cited records:
FND-B440C1BF: Unassessed program risk of O-ring substitution for OEM rectangular-slot gasket · L4 · rating 4
FND-1A251687: Chronic gasket failure on 310FT01 left to routine resealing — no OEM spares, root-cause or replacement programme · L4 · rating 4
FND-6155A1C2: F&G detection system had no auto-shutdown or fire-suppression interlock · L4 · rating 4
FND-A443D288: O-ring substitution - regular practice tolerated and modelled by supervisors · L3 · rating 4
FND-1280E788: Breakdown-maintenance philosophy for electrical/flame-proof equipment in Zone 1 areas · L4 · rating 4
FND-82761CC5: No delegated authority or criteria for emergency isolation in DMP and night-shift structure · L4 · rating 4
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
FND-5919B328: Authorised return-to-service without the mandatory hydrostatic test · L3 · rating 4
FND-850B270C: External safety audit recommendations overdue without required approval for extensions · L3 · rating 2

## Slide 20
How the site set this up
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme
L3 SVF 3.4 Failed to Mitigate/ Ineffective Action against Identified Risk
L3 SVV 4.1 Failure to Enforce Existing Rules (Supervisory act of Omission)
L3 SVI 1.1 Leadership/Supervisory Oversight Inadequate
L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly
L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance
L2 PTE 2.7 Technical Guidance is Unclear/Unavailable or Incorrect
L4 OIC 2.1 Organizational Culture Allows for Unsafe Task/Mission
L1 AV 1.1 Violation - Routine/Widespread
L4 OIC 2.7 Inconsistent Risk Management Practices
L1 AJDE 2.11 Misapplied or unaware of existing Policy/Procedure
L3 SVI 1.6 Lack of Supervisory Response to Critical Information
L3 SVV 4.5 No Action/ Mitigation Measures for Identified Risk
L4 OIR 1.1 Command and Control Resources are Deficient
L2 PTE 2.11 Equipment Not configured Correctly
L2 PTE 2.6 System Automation or System Redundancy
L4 OIR 1.5 Failure in Timely Acquisition/ Procurement/ Upgrade
Notes: Nodes: L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme; L3 SVF 3.4 Failed to Mitigate/ Ineffective Action against Identified Risk; L3 SVV 4.1 Failure to Enforce Existing Rules (Supervisory act of Omission); L3 SVI 1.1 Leadership/Supervisory Oversight Inadequate; L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly; L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance; L2 PTE 2.7 Technical Guidance is Unclear/Unavailable or Incorrect; L4 OIC 2.1 Organizational Culture Allows for Unsafe Task/Mission; L1 AV 1.1 Violation - Routine/Widespread; L4 OIC 2.7 Inconsistent Risk Management Practices; L1 AJDE 2.11 Misapplied or unaware of existing Policy/Procedure; L3 SVI 1.6 Lack of Supervisory Response to Critical Information; L3 SVV 4.5 No Action/ Mitigation Measures for Identified Risk; L4 OIR 1.1 Command and Control Resources are Deficient; L2 PTE 2.11 Equipment Not configured Correctly; L2 PTE 2.6 System Automation or System Redundancy; L4 OIR 1.5 Failure in Timely Acquisition/ Procurement/ Upgrade
- L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme → L3 SVF 3.4 Failed to Mitigate/ Ineffective Action against Identified Risk (7 mentions)
- L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme → L3 SVV 4.1 Failure to Enforce Existing Rules (Supervisory act of Omission) (6 mentions)
- L3 SVI 1.1 Leadership/Supervisory Oversight Inadequate → L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly (6 mentions)
- L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance → L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly (6 mentions)
- L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance → L2 PTE 2.7 Technical Guidance is Unclear/Unavailable or Incorrect (6 mentions)
- L4 OIC 2.1 Organizational Culture Allows for Unsafe Task/Mission → L1 AV 1.1 Violation - Routine/Widespread (5 mentions)
- L4 OIC 2.7 Inconsistent Risk Management Practices → L1 AJDE 2.11 Misapplied or unaware of existing Policy/Procedure (5 mentions)
- L4 OIC 2.7 Inconsistent Risk Management Practices → L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly (5 mentions)
- L4 OIC 2.7 Inconsistent Risk Management Practices → L3 SVI 1.6 Lack of Supervisory Response to Critical Information (5 mentions)
- L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme → L3 SVI 1.6 Lack of Supervisory Response to Critical Information (5 mentions)
- L4 OIR 1.6 Failure in Maintenance/ Spares/ Support Programme → L3 SVV 4.5 No Action/ Mitigation Measures for Identified Risk (5 mentions)
- L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance → L1 AJDE 2.11 Misapplied or unaware of existing Policy/Procedure (5 mentions)
- L3 SVV 4.1 Failure to Enforce Existing Rules (Supervisory act of Omission) → L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly (5 mentions)
- L4 OIC 2.1 Organizational Culture Allows for Unsafe Task/Mission → L1 ASBE 1.2 Checklist Not Followed/Not Followed Correctly (4 mentions)
- L4 OIC 2.1 Organizational Culture Allows for Unsafe Task/Mission → L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance (4 mentions)
- L4 OIC 2.7 Inconsistent Risk Management Practices → L1 AV 1.1 Violation - Routine/Widespread (4 mentions)
- L4 OIC 2.7 Inconsistent Risk Management Practices → L3 SVI 1.4 Failed to Provide Appropriate Policy/ Guidance (4 mentions)
- L4 OIR 1.1 Command and Control Resources are Deficient → L2 PTE 2.11 Equipment Not configured Correctly (4 mentions)
- L4 OIR 1.1 Command and Control Resources are Deficient → L2 PTE 2.6 System Automation or System Redundancy (4 mentions)
- L4 OIR 1.5 Failure in Timely Acquisition/ Procurement/ Upgrade → L2 PTE 2.11 Equipment Not configured Correctly (4 mentions)
Cites: FND-02310148; FND-031A3738; FND-044D1DEC; FND-0B651843; FND-0D4C2C13; FND-0FFC03BB; FND-119E6CF7; FND-137BC719; FND-14D093BD; FND-14E2A4B5; FND-1A251687; FND-1DF986F8; FND-257C1100; FND-2B215AA5; FND-304A499A; FND-30EC643B; FND-35279095; FND-3746C7B6; FND-3A34BAD3; FND-3AB996FC; FND-3FEE59DF; FND-403FD778; FND-4458E0C0; FND-4DAC9500; FND-4F687CC5; FND-50C7319E; FND-535125C1; FND-53C9BDB5; FND-5BA62765; FND-5E08D0F8; FND-5EA23B17; FND-6155A1C2; FND-62EF1667; FND-678E51A3; FND-6ECCE231; FND-72A7D26C; FND-730D0DCA; FND-76A6DEC1; FND-78ED8552; FND-7E1F2B3F; FND-7F829BEB; FND-82FC718D; FND-83AD4621; FND-856F80CE; FND-89D53630; FND-934DCBE1; FND-9E1AB5BA; FND-9F27F129; FND-A3DCEBD8; FND-ABF11182; FND-ADC25F29; FND-B86F67F0; FND-B93AE333; FND-B955FBD6; FND-C4B133AA; FND-C4E06264; FND-C5000A82; FND-C9C77FB7; FND-D1709E71; FND-D58142C9; FND-D9A35E88; FND-DF1144C3; FND-E885ED4C; FND-EB48C68C; FND-EBB66554; FND-F7FE8463; FND-FA73D914; FND-FD98468B
Cited records:
FND-02310148: Emergency isolation MOVs never upgraded for remote operation from the control room · L4 · rating 4
FND-031A3738: Permit-to-work/JSA policy was incomplete: missing permits untracked and Job Safety Plans not attached in SAP · L3 · rating 2
FND-044D1DEC: Emergency isolation valves MOV 54 and the Gas Terminal MOVs were local-manual only, with no remote control from the control room · L4 · rating 4
FND-0B651843: Calibration programme executed without checklist or recorded setpoint change on meter 310FT01 (Dec-2019) · L4 · rating 3
FND-0D4C2C13: No pressure data available from metering-line transmitters 310PT4/310PT5/310PT6 · L4 · rating 3
FND-0FFC03BB: Metering-line pressure transmitters (310PT4/5/6) never commissioned for DCS data acquisition · L4 · rating 3
FND-119E6CF7: F&G detection system not interlocked to automatic shutdown or suppression · L4 · rating 4
FND-137BC719: No SOP for calibration and return-to-service of high-pressure meters · L3 · rating 4
FND-14D093BD: Control-room emergency readiness risk accepted with 4-day training and no defined qualification · L4 · rating 3
FND-14E2A4B5: Missing work permits untracked and Job Safety Plans absent from SAP · L4 · rating 2
FND-1A251687: Chronic gasket failure on 310FT01 left to routine resealing — no OEM spares, root-cause or replacement programme · L4 · rating 4
FND-1DF986F8: Permit-to-work lifecycle oversight · L3 · rating 2
FND-257C1100: No standard operating procedure existed for calibration and return-to-service of the high-pressure meters, including mandatory hydrotest to design pressure · L3 · rating 4
FND-2B215AA5: DCS clocks across control rooms drifted by 2-12 minutes · L4 · rating 2
FND-304A499A: Self-Safety Audit oversight - generic checklist and unverified compliance · L3 · rating 3
FND-30EC643B: Post-incident electrical PM audit grouped nine lamps into one generic status · L4 · rating 2
FND-35279095: Internal and self-safety audit checklist completeness rules not enforced · L3 · rating 3
FND-3746C7B6: Maintenance supervision - 18-Sep-2020 gasket replacement of meter 310FT01 · L3 · rating 4
FND-3A34BAD3: Meter 310FT01 gasket replacement recurrence treated as routine maintenance · L4 · rating 4
FND-3AB996FC: Return-to-service after gasket replacement without design-pressure hydrostatic test · L4 · rating 4
FND-3FEE59DF: MOC procedure published August 2016 but not implemented since 2018 · L4 · rating 3
FND-403FD778: Calibration documentation and checklist rules not enforced during Dec-2019 calibration of 310FT01 · L3 · rating 3
FND-4458E0C0: F&G detection system never upgraded to automatic shutdown/suppression interlock · L4 · rating 4
FND-4DAC9500: 1.03 mm wall loss with heavy pitting on zero-corrosion-allowance 36-inch segment remediated with painting only · L4 · rating 3
FND-4F687CC5: DMP/ERDMP omitted isolation and stoppage decision criteria · L3 · rating 4
FND-50C7319E: No post-maintenance hydrotest or return-to-service SOP for high-pressure meter gasket work · L4 · rating 4
FND-535125C1: Work-permit and Job Safety Plan policy gaps · L3 · rating 2
FND-53C9BDB5: Work permit/JSA system missing permits and Job Safety Plans · L4 · rating 2
FND-5BA62765: 2018 and 2019 internal safety audits issued observations without filled checklists · L4 · rating 2
FND-5E08D0F8: Breakdown-skewed electrical preventive-maintenance culture left compromised HPMV FLP lamp in service · L4 · rating 4
FND-5EA23B17: 2017 pipeline thickness-loss findings left without corrective action for 3 years · L4 · rating 3
FND-6155A1C2: F&G detection system had no auto-shutdown or fire-suppression interlock · L4 · rating 4
FND-62EF1667: SAP Notification 3800419840 left open and unreviewed · L4 · rating 3
FND-678E51A3: SAP maintenance-work closure loop broken — notification 3800419840 never closed or reviewed · L4 · rating 3
FND-6ECCE231: Management of Change policy published in August 2016 was not implemented, with no MOCs since 2018 · L3 · rating 3
FND-72A7D26C: No material specification or procurement policy for pressure-boundary gaskets · L3 · rating 4
FND-730D0DCA: DMP/ERDMP hydrocarbon-leak guidance omitted isolation and stoppage criteria · L4 · rating 4
FND-76A6DEC1: Generic non-plant-specific self-safety audit checklist and unavailable manuals/SOPs · L3 · rating 3
FND-78ED8552: Inadequate control-room training and qualification policy · L3 · rating 3
FND-7E1F2B3F: Work permit and Job Safety Plan requirements not enforced for maintenance execution · L3 · rating 3
FND-7F829BEB: December 2019 calibration setpoint changes undocumented and checklist-free · L4 · rating 3
FND-82FC718D: Recurring gasket failures on 310FT01 treated as routine maintenance instead of reliability warning · L4 · rating 4
FND-83AD4621: Metering-system P&ID lost, vendor replacement unapproved and field configuration mismatched · L4 · rating 2
FND-856F80CE: 12 external-audit recommendations overdue without Director Offshore approval · L4 · rating 2
FND-89D53630: Instrument/calibration supervision - Dec-2019 unsigned setpoint change · L3 · rating 3
FND-934DCBE1: Single PELCO PTZ D5230D camera with ~90-second pan provided the only CCTV coverage and was lost at ignition · L4 · rating 3
FND-9E1AB5BA: Generic, unverified audit checklist culture · L4 · rating 3
FND-9F27F129: Internal safety audits lacked filled checklists and completed audit coverage · L3 · rating 2
FND-A3DCEBD8: Pipeline thickness-monitoring programme off cadence and 2017 corrective-action findings left unplanned for 3+ years · L4 · rating 3
FND-ABF11182: Breakdown-skewed electrical preventive-maintenance programme — Zone-1 HPMV FLP lamp left with compromised flame-proof integrity · L4 · rating 4
FND-ADC25F29: Flame-proof lamp integrity and electrical PM rules not enforced in Zone 1 — probable ignition source · L3 · rating 4
FND-B86F67F0: Regular use of locally procured O-rings for the 1986 rectangular-slot meter gasket · L4 · rating 4
FND-B93AE333: Internal Safety Audits 2018-2019 - no filled checklists · L3 · rating 3
FND-B955FBD6: Diesel fire-water pump fleet left degraded — two under maintenance, one 2-minute tripping fault undiagnosed · L4 · rating 2
FND-C4B133AA: No baseline pipeline-thickness data and missing original drawings/schedules · L3 · rating 2
FND-C4E06264: Post-repair hydrostatic test requirement not enforced on 18-Sep-2020 gasket replacement · L3 · rating 4
FND-C5000A82: Annunciator-only detector display and absent DCS historisation delayed the first control-room alarm by ~7 minutes · L4 · rating 3
FND-C9C77FB7: Self-safety audit used generic non-plant-specific checklist · L4 · rating 3
FND-D1709E71: Electrical preventive-maintenance oversight - FLP lamp integrity in Zone 1 · L3 · rating 3
FND-D58142C9: No checklist provided for critical high-pressure calibration jobs · L3 · rating 3
FND-D9A35E88: DCS time-synchronisation drift across control rooms never corrected · L4 · rating 2
FND-DF1144C3: DMP/ERDMP omitted isolation/stoppage decision criteria and authority · L4 · rating 4
FND-E885ED4C: Permit-to-work records incomplete — missing permits untracked, Job Safety Plans absent from SAP, closure unreviewed · L4 · rating 2
FND-EB48C68C: MOC policy published but not implemented since 2018 · L3 · rating 3
FND-EBB66554: Locally sourced O-ring substitution without specification, QC or recorded authority · L4 · rating 4
FND-F7FE8463: Management of Change policy not implemented since 2018, allowing unapproved material substitution · L4 · rating 4
FND-FA73D914: 36-inch pipeline pitting and 1.03 mm metal loss addressed by painting only · L4 · rating 3
FND-FD98468B: Undocumented calibration setpoint changes with no checklist on meter 310FT01 · L4 · rating 3

## Slide 21
Coverage
This pack cites 39 of 62 relevant findings.
25 of 35 top-rated relevant findings cited.
Learning purposes: not a statutory document. Draft learnings from a ProbeMatrix investigation export; validate them before adoption. · Learnings drafted by an AI agent from AI-assisted findings
Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
Learning purposes: not a statutory document · Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
DRAFT
Notes: This pack cites 39 of 62 relevant findings.
25 of 35 top-rated relevant findings cited.
Learning purposes: not a statutory document. Draft learnings from a ProbeMatrix investigation export; validate them before adoption. · Learnings drafted by an AI agent from AI-assisted findings
Generated with ProbeMatrix Learnings Coach v2.0.0a8 (open source, MIT) from a ProbeMatrix four-level human-factors investigation. ProbeMatrix by Eyekyam: ashley@eyekyam.com
Left out on purpose:
- FND-44219027: Left out of the Learnings Register after a reviewer downgrade vote; the vote is recorded in the register's source note, not in this export. Left out here for the same reason.
Gaps in the evidence:
- [GAP] The export does not show whether the repeat seal failures, the 2017 thickness findings or the unused change procedure were ever reported to the site leadership team. [FND-1A251687; FND-0F19C9FC; FND-8083ECAC]
Evidence needed: Site leadership meeting minutes and management-review records for 2018 to 2020.
Limits of this pack:
- A management-review input table is not included; add it when the debrief feeds a management review.
- The analysis is a desk review of the published enquiry report; it had no site access or interviews.
- Site authority limits are not in the export; decisions marked 'Needs corporate decision' assume capital above them.